## BOM Order Sheet
SOLAR INSTALLATION - ORDER SHEET
Project: Jeffrey Hanson - 7266 14th St N ¦ Generated: April 14, 2026 14:33
# | Item / Description | Part Number | Manufacturer | Qty | Unit
1 | job_name |  |  | Jeffrey Hanson - 7266 14th St N | EA
2 | address |  |  | 7266 14th St N, St. Petersburg, FL 33702 | EA
3 | ahj |  |  | Pinellas County | EA
4 | utility |  |  | DUKE ENERGY | EA
5 | system_dc_kw |  |  | 11.61 | EA
6 | system_ac_kw |  |  | 9.42 | EA
7 | panel_count |  |  | 27 | EA
8 | panel_orientation |  |  | landscape | EA
9 | roof_type |  |  | asphalt/composite shingle | EA
10 | mounting_system |  |  | IronRidge XR-10 | EA
11 | installation_type |  |  | Pitched Roof Mount | EA
12 | date_prepared |  |  | 2026-01-16 | EA
13 | engineer |  |  | D. Chad Godwin PE 81360 | EA
14 | array_layout |  |  | 3 strings x 9 modules | EA
15 | roof_1_modules |  |  | 13 | EA
16 | roof_2_modules |  |  | 14 | EA
17 | total_rail_length_ft |  |  | 242 | EA
18 | total_array_area_sqft |  |  | 566.98 | EA
19 | roof_coverage_pct |  |  | 36.16 | EA
20 | line_1_qty |  |  | 27 | EA
21 | line_1_desc |  |  | Solar Panels - Q.TRON BLK M-G2+/AC 430W | EA
22 | line_1_pn |  |  | SEE-ENGINEERING | EA
23 | line_2_qty |  |  | 27 | EA
24 | line_2_desc |  |  | Integrated Microinverters - Q.MI.349B-G1 240V | EA
25 | line_2_pn |  |  | SEE-ENGINEERING | EA
26 | line_3_qty |  |  | 18 | EA
27 | line_3_desc |  |  | Rail Sticks 14.0ft IronRidge XR-10 | EA
28 | line_3_pn |  |  | XR-10-168M | EA
29 | line_4_qty |  |  | 9 | EA
30 | line_4_desc |  |  | Splice Kits XR-10 | EA
31 | line_4_pn |  |  | XR-10-SP | EA
32 | line_5_qty |  |  | 61 | EA
33 | line_5_desc |  |  | Mounting Feet Comp Shingle Flashing | EA
34 | line_5_pn |  |  | FW-LFAB-200B | EA
35 | line_6_qty |  |  | 61 | EA
36 | line_6_desc |  |  | T-Bolts Clicker Bolts | EA
37 | line_6_pn |  |  | HS-T-BLT-0100 | EA
38 | line_7_qty |  |  | 183 | EA
39 | line_7_desc |  |  | Stainless Hex Screws M8 | EA
40 | line_7_pn |  |  | HS-M8-SS | EA
41 | line_8_qty |  |  | 48 | EA
42 | line_8_desc |  |  | Mid Clamps 2-rail between panels | EA
43 | line_8_pn |  |  | CLM-0003B | EA
44 | line_9_qty |  |  | 12 | EA
45 | line_9_desc |  |  | End Clamps per row termination | EA
46 | line_9_pn |  |  | CLM-0002B | EA
47 | line_10_qty |  |  | 1 | EA
48 | line_10_desc |  |  | Zip Ties 10-inch | EA
49 | line_10_pn |  |  | ZIPTIE-10IN-PK | EA
50 | line_11_qty |  |  | 3 | EA
51 | line_11_desc |  |  | Ground Lugs copper 1 per row | EA
52 | line_11_pn |  |  | GR-LUG-100 | EA
53 | line_12_qty |  |  | 24 | EA
54 | line_12_desc |  |  | Q.CELLS AC Daisy-Chain Cable module-to-module | EA
55 | line_12_pn |  |  | QCELLS-ACCABLE | EA
56 | line_13_qty |  |  | 6 | EA
57 | line_13_desc |  |  | Q.CELLS Branch Circuit Terminator Caps | EA
58 | line_13_pn |  |  | QCELLS-TERMCAP | EA
59 | line_14_qty |  |  | 3 | EA
60 | line_14_desc |  |  | Q.CELLS Combiner Branch Leads 1 per string | EA
61 | line_14_pn |  |  | QCELLS-LEAD | EA
62 | line_15_qty |  |  | 1 | EA
63 | line_15_desc |  |  | 15A/2P Breaker inside combiner box | EA
64 | line_15_pn |  |  | BR115 | EA
65 | line_16_qty |  |  | 3 | EA
66 | line_16_desc |  |  | 20A Eaton BR 2-Pole Breaker per string | EA
67 | line_16_pn |  |  | BR220 | EA
68 | ac_disconnect_type |  |  | Visible-Open Lockable Fused | EA
69 | ac_disconnect_rating |  |  | 60A 240V NEMA 3R | EA
70 | ac_disconnect_qty |  |  | 1 | EA
71 | ac_disconnect_status |  |  | NEW | EA
72 | ac_disconnect_notes |  |  | 2x 50A fuses within 5 ft of meter | EA
73 | combiner_model |  |  | Q.CELLS Q.HOME COMBINER 80 G1 | EA
74 | combiner_rating |  |  | 125A 1-Phase 3-Wire 120V/240V | EA
75 | combiner_qty |  |  | 1 | EA
76 | combiner_status |  |  | NEW | EA
77 | combiner_notes |  |  | Contains 1x 15A/2P breaker | EA
78 | main_service_breaker |  |  | 200A/2P | EA
79 | main_service_rating |  |  | 200A 240V | EA
80 | main_service_qty |  |  | 1 | EA
81 | main_service_status |  |  | EXISTING | EA
82 | main_service_notes |  |  | No upgrade required | EA
83 | grounding_type |  |  | 6 AWG bare copper | EA
84 | grounding_connection |  |  | Bonded to existing GES | EA
85 | grounding_status |  |  | EXISTING | EA
86 | grounding_notes |  |  | Per NEC 690 and 250.122 | EA
87 | rapid_shutdown |  |  | EQUIPPED NEC 690.56(C) | EA
88 | battery_storage |  |  | NONE utility-interactive only | EA
89 | subpanel_upgrade |  |  | NOT REQUIRED | EA
90 | main_panel_upgrade |  |  | NOT REQUIRED | EA
91 | interconnection_type |  |  | Load-side NEC 705.12 | EA
92 | fire_setbacks |  |  | Zone 1: 4ft Zones 2-3: 3ft | EA
93 | roof_penetrations |  |  | Flashed and sealed per code | EA
94 | design_wind_speed |  |  | 150 mph Exposure Category C | EA
95 | snow_load |  |  | 3 PSF | EA
96 | roof_material |  |  | Asphalt/Composite Shingle | EA
97 | rafter_spacing |  |  | 2x4 @ 24 OC | EA
ELECTRICAL EQUIPMENT (from engineering sheet - add quantities manually)
1 | Main Breaker (existing or new) |  |  |  | EA
2 | PV System Breaker |  |  |  | EA
3 | AC Disconnect (fused / non-fused) |  |  |  | EA
4 | Fuse Size |  |  |  | EA
5 | Combiner Box |  |  |  | EA
6 | AC Combiner / Load Center |  |  |  | EA
7 | Conduit (specify type and size) |  |  |  | EA
8 | Wire - Solar (specify AWG) |  |  |  | EA
9 | Wire - AC (specify AWG) |  |  |  | EA
10 | Other |  |  |  | EA